## Slide 1: PMC-592 Web Interface
September 29, 2016

## Slide 2
Overview
Main Menu
6 functions
1. Status
2. Metering
3. Alarm Status
4. Event Log
5. Setup
6. Diagnostics

## Slide 3
Status— Global Status
Enter the IP Address of the PMC-592 in the Address area of your Internet Explorer.
Default User Name: user
Default Password: 0000
Measurements:
Run Time
Latest Alarm Channel
Event Logs
DI Status
DO Status

## Slide 4
Metering — Real-Time — Mains
Measurements:
Mains I/II Voltage
Voltage
Frequency
Mains I/II Current
I Per Phase and Average
Neutral Current
Loading
Mains I/II Power
kW
kvar
kVA
PF
Mains I/II Unbalance
Mains I/II RTD1/2 Temperature
Ia/Ib/Ic

## Slide 5
Metering — Real-Time — Branches
Measurements:
1-Phase SM1 to SM42 Current
1-Phase SM1 to SM42 Loading
1-Phase SM1 to SM42 kW
1-Phase SM1 to SM42 kvar
1-Phase SM1 to SM42 kVA
1-Phase SM1 to SM42 PF
Measurements:
1-Phase SM43 to SM84 Current
1-Phase SM43 to SM84 Loading
1-Phase SM43 to SM84 kW
1-Phase SM43 to SM84 kvar
1-Phase SM43 to SM84 kVA
1-Phase SM43 to SM84 PF

## Slide 6
Metering — Real-Time — Branches
Measurements:
2-Phase SM1 to SM42 Current
2-Phase SM1 to SM42 Loading
2-Phase SM1 to SM42 kW
2-Phase SM1 to SM42 kvar
2-Phase SM1 to SM42 kVA
2-Phase SM1 to SM42 PF
Measurements:
3-Phase SM1 to SM28 Current
3-Phase SM1 to SM28 Loading
3-Phase SM1 to SM28 kW
3-Phase SM1 to SM28 kvar
3-Phase SM1 to SM28 kVA
3-Phase SM1 to SM28 PF

## Slide 7
Measurements:
VM1 to VM10 kW
Metering — Real-Time — Virtual Meter

## Slide 8
Measurements:
Mains I/II kWh Imp
Mains I/II kWh Exp
Mains I/II kvarh Imp
Mains I/II kvarh Exp
Mains I/II kVAh Total
Reset:
Click the broom icon of Reset All can clear all energy measurements.
Metering — Energy — Mains

## Slide 9
Metering — Energy — Branches
Measurements:
1-Phase SM1 to SM42 kWh
1-Phase SM1 to SM42 kvarh
1-Phase SM1 to SM42 kVAh
Measurements:
1-Phase SM43 to SM84 kWh
1-Phase SM43 to SM84 kvarh
1-Phase SM43 to SM84 kVAh

## Slide 10
Metering — Energy — Branches
Measurements:
1-Phase SM1 to SM42 kWh
1-Phase SM1 to SM42 kvarh
1-Phase SM1 to SM42 kVAh
Measurements:
1-Phase SM1 to SM28 kWh
1-Phase SM1 to SM28 kvarh
1-Phase SM1 to SM28 kVAh

## Slide 11
Metering — Energy — Virtual Meter
Measurements:
VM1 to VM10 kWh

## Slide 12
Metering — Demand — Mains
Demand Type:
Click the drop-down button to choose the Demand type you want to view.
Present Demand
Historical Max Demand
Max Demand of This Month
Max Demand of Last Month
Measurements:
Ia/Ib/Ic
kW
kvar
kVA

## Slide 13
Metering — Demand — Branches
Measurements:
1-Phase SM1 to SM42 Current Demand
1-Phase SM1 to SM42 kW Demand
1-Phase SM1 to SM42 kvar Demand
1-Phase SM1 to SM42 kVA Demand
Measurements:
1-Phase SM43 to SM84 Current Demand
1-Phase SM43 to SM84 kW Demand
1-Phase SM43 to SM84 kvar Demand
1-Phase SM43 to SM84 kVA Demand

## Slide 14
Metering — Demand — Branches
Measurements:
2-Phase SM1 to SM42 Current Demand
2-Phase SM1 to SM42 kW Demand
2-Phase SM1 to SM42 kvar Demand
2-Phase SM1 to SM42 kVA Demand
Measurements:
3-Phase SM1 to SM28 Current Demand
3-Phase SM1 to SM28 kW Demand
3-Phase SM1 to SM28 kvar Demand
3-Phase SM1 to SM28 kVA Demand

## Slide 15
Metering — Demand — Temperature
Measurements:
RTD1/RTD2 Temperature Demand

## Slide 16
Metering — Harmonics — Mains
Measurements:
Mains-I/II Current 2nd to 31st Harmonic
Mains-I/II Voltage 2nd to 31st Harmonic
Mains-I/II Current THD/TOHD/TEHD
Mains-I/II Voltage THD/TOHD/TEHD

## Slide 17
Metering — Harmonics — Branches
Measurements:
SM1 to SM84 Current THD

## Slide 18
Metering — Max/Min — Mains
Max/Min Type:
Click the drop-down button to choose the max/min type you want to view
Historical Max
Historical Min
Max of This Month
Max of Last Month
Min of This Month
Min of Last Month.
Measurements:
Voltage Max/Min
Current Max/Min
Power Max/Min
Power Voltage Unbalance Max/Min
Current Unbalance Max/Min
RTD1/RTD2 Max/Min

## Slide 19
Metering — Max/Min — Branches
Measurements:
1-Phase SM1 to SM42 Current Max/Min
1-Phase SM1 to SM42 Loading Max/Min
1-Phase SM1 to SM42 kW Max/Min
1-Phase SM1 to SM42 kvar Max/Min
1-Phase SM1 to SM42 kVA Max/Min
1-Phase SM1 to SM42 PF Max/Min
Measurements:
1-Phase SM43 to SM84 Current Max/Min
1-Phase SM43 to SM84 Loading Max/Min
1-Phase SM43 to SM84 kW Max/Min
1-Phase SM43 to SM84 kvar Max/Min
1-Phase SM43 to SM84 kVA Max/Min
1-Phase SM43 to SM84 PF Max/Min

## Slide 20
Metering — Max/Min — Branches
Measurements:
2-Phase SM1 to SM42 Current Max/Min
2-Phase SM1 to SM42 Loading Max/Min
2-Phase SM1 to SM42 kW Max/Min
2-Phase SM1 to SM42 kvar Max/Min
2-Phase SM1 to SM42 kVA Max/Min
2-Phase SM1 to SM42 PF Max/Min
Measurements:
3-Phase SM1 to SM28 Current Max/Min
3-Phase SM1 to SM28 Loading Max/Min
3-Phase SM1 to SM28 kW Max/Min
3-Phase SM1 to SM28 kvar Max/Min
3-Phase SM1 to SM28 kVA Max/Min
3-Phase SM1 to SM28 PF Max/Min

## Slide 21
Metering — Max/Min — PQ
Measurements:
Mains-I/II Voltage THD/TOHD/TEHD Max/Min
Mains-I/II Current THD/TOHD/TEHD Max/Min
Measurements:
SM1 to SM84 THD Max/Min

## Slide 22
Metering — I/O
Measurements:
DI Status
DO Status

## Slide 23
Alarm Status — Instantaneous Alarm
Measurements:
Mains-I/II Global Alarm
Mains-I/II Voltage Alarm
Mains-I/II Current Alarm
Mains-I/II Power Alarm
Mains-I/II Harmonics Alarm
Mains-I/II Unbalance Alarm
Mains-I/II DI Alarm
Mains-I/II Temperature Alarm
Measurements:
SM1 to SM84 Alarm Status

## Slide 24
Alarm Status — Latched Alarm
Measurements:
Mains-I/II Global Alarm
Mains-I/II Voltage Alarm
Mains-I/II Current Alarm
Mains-I/II Power Alarm
Mains-I/II Harmonics Alarm
Mains-I/II Unbalance Alarm
Mains-I/II DI Alarm
Mains-I/II Temperature Alarm
Measurements:
SM1 to SM84 Alarm Status

## Slide 25
Alarm Status — Alarm Count
Measurements:
All Mains Alarm Count
Clear the count to zero by click the erase icon after every Alarm Count
Measurements:
SM1 to SM84 Alarm Count
Clear the count to zero by click the erase icon after every Alarm Count

## Slide 26
Event Log — SOE
Six Types of SOE:
All
DI
DO
Alarm
Operation
Self-Check
Channel of Alarm SOE:
Mains-I/II Power
Mains-I/II Voltage
Mains-I/II Current
Mains-I/II Voltage Unbalance
Mains-I/II Current Unbalance
Frequency
RTD1/RTD2
DI1/DI2
SM1 to SM84 Current
You can quickly find the SOE you want to check by set the Start Time and End Time in the red rectangle area of the above picture.

## Slide 27
Event Log — Waveform
Click Waveform on the left-hand pane and the following screen appears on the right-hand pane.
Waveform File with format CFG or DAT can be downloaded.
Click Clear All to clear all
Waveform Logs.

## Slide 28
Setup — Basic Setup
Measurements:
System Basic Settings

## Slide 29
Measurements:
Panel Name Settings
Device Name Settings
Setup — Panel Name Setup

## Slide 30
Setup — Branch Setup
Measurements:
CT Strips Installation Mode Settings
CT Strips Phases Settings
CT Strips Direction Settings
CT Strips Polarity Settings

## Slide 31
Setup — Virtual Meter Setup
Measurements:
VM 1 to VM 10 Virtual Meters Settings

## Slide 32
Setup — Breaker Meter Setup
Measurements:
Mains I/II Breaker Rating Settings

## Slide 33
Setup — Alarm Setup
Measurements:
Current Alarm Settings
Voltage Alarm Settings

## Slide 34
Setup — Alarm Setup
Measurements:
Power Alarm Settings
PQ Alarm Settings

## Slide 35
Setup — Alarm Setup
Measurements:
Misc Settings
PF
Temperature
DI
Phase Reversal Alarm

## Slide 36
Setup — Communication
Measurements:
P1Communication Parameters
P2 Communication Parameters
P3 Communication Parameters
Email Settings
SNMP Settings

## Slide 37
Setup — Record Setup
Measurements:
WFR Settings
Energy Log Settings

## Slide 38
Setup — Clock Setup
Measurements:
Device Time Settings
SNTP Time Sync Settings

## Slide 39
Setup — Password and Clear & Reset Setup
Measurements:
You can clear or reset the following logs
All Latched Alarms
All Alarm Counters
Energy’s
Max Demand log
Max/Min Log, SOE, WFR and Energy Logs
Measurements:
Device Password Settings

## Slide 40
Diagnostics — About
Measurements:
System Overview
Self-Test Diagnostic

## Slide 41
Diagnostics — Maintenance
Measurements:
Backup
Restore
Measurements:
Factory Defaults

## Slide 42
Diagnostics — Maintenance
Measurements:
Firmware Upgrade
Measurements:
Reboot
Alarm E-mail Test
SNMP MIB Download